HOW TO WIRE

THE ARMOURFLASH TS ARM120 SOUNDER/STROB TO THE WSM UNIT.

(TIP)

PROGRAMME THE WSM TO THE  INFINITE PANEL BEFORE FITTING AND CONNECTING TO THE SONADE SOUNDER.

TERMINAL (+)  Of the WSM unit goes to TERMINAL (HOLD OFF +) 
On the TS ARM120 (TIP) RED WIRE

TERMINAL (-)     Of the WSM unit goes to TERMINAL (HOLD OFF -) 
On the TS ARM120     (TIP) BLACK WIRE

TERMINAL (-T)   Of the WSM unit goes to TERMINAL (TRIG -) 
On the TS ARM120    (TIP) BLUE WIRE

TERMINAL (-S)   Of the WSM unit goes to TERMINAL ( STROBE -) 
On the TS ARM120 (TIP) YELLOW WIRE

FIT A WIRE LINK INSIDE THE ARMOURFLASH FROM TERMINAL (HOLD OFF +) TO TERMINAL STROBE (+)

(TIP) RED LINK WIRE

ONCE ALL WIRES ARE CONNECTED PLUG IN MAINS TRANSFORMER TO THE WSM

CONNECT THE BATTERY IN THE ARMOURFLASH TO THE TERMINALS MARKED J1 (+) (-)

NOTE THE SOUNDER WILL NOW SOUND UNTILL THE COVER IS FITTED

REMOVE THE RED LINK IN THE ARMOURFLASH.

FIT THE TWO PLUGS FROM THE COVER THE LED ON THE LID SOULD NOW BE ON.

FIT THE COVER THE SOUNDER SHOULD NOW STOP.THE LED SHOULD REMAIN ON.

TEST SOUNDER.

NOTE:- THE EXTERNAL SOUNDER TEST WILL ONLY TEST THE SOUNDER AND NOT THE STROBE.

.