## INSTALLATION GUIDE

Connecting detectors & call-points to a zone:

+ in	    + out         	     + in	      + out	        + in	+ out	          + in	   + out		+ in	 + out

+

# PANEL

_

- in	    - out		 - in	          - out	        - in	- out		- in	   - out	        - in	     - out	       END OF LINE MODULE

Connecting only call-points to a zone:

+ in	    + out         	     + in	      + out	        + in	+ out

+

# PANEL															   END OF LINE MODULE

_

- in	    - out		     - in	      - out	        - in	- out

Connecting detectors only to a zone:

+ in	    + out         	     + in	      + out	        + in	+ out	          + in	  + out

+

# PANEL

_

- in	    - out		 - in	          - out	        - in	- out		- in	   - out	                    END OF LINE MODULE

 The Mag panel recognises 470 ohms as fire condition.

 It is recommended that all detection devices that are used on a Mag panel are fitted with a 470 ohms monitoring resistor as standard.

 All detector bases should be fitted with a SCHOTTKY diode (diode type: BYV-1060)