Chocbox - specification sheet

Item:

Description:

Dimensions:

Materials:

Test Specification:

Cable Restraint:

Flammable Material:

CHOCBOX Inline Connector / Junction Box

A plastic box to insulate connector blocks.

Used as a junction box for fixed wiring.

Used as an inline connector when used with cord grips supplied.

90mm x 50mm x 30mm

Polyproperlene.

Partial test to appropriate Clauses of BS4533: section

102.1:1990/EN60 598-2-1:1989 in respect of cable restraint and

flammability of material.

The cable restraint clamping screws were tightened and loosened

5 times at 0.6Nm torque.  No damage occurred impairing further

use of the screws.

Cable restraints withstood a pull-force 60N, applied 25 times

The sample material was subjected to the 650 degree glow-wire

test of Sub-clause 13.3.2 of BSEN60598-1 using the test

apparatus and test procedure described in IEC 695-2-1:1990 (fire

hazard testing for electrotechnical products).

After testing, the sample was examined with respect to 650

degree glow-wire test covers, shades and similar parts not having

an insulation function referred to in Clause 4.15 of BSEN60598-1.

422-01-04 referring to 526-03-02 (see attached regs.)